## Sheet1
SORT | CATEGORY | VIOLATION CODE | ASSOCIATED RULES | QUESTION | SIGNIF | REEVALUATION | RULE CAT
87 | Aboveground | 7001 | 62-762.101(5) | No reasonable access provided. | Minor | Inspection | 62-762
88 | Aboveground | 7002 | 62-762.401(1)(b), 62-762.401(2), 62-762.401(3)(a), 62-762.401(3)(a), 62-762.401(3)(b), 62-762.401(3)(c) | Registration Form not submitted fora new system, change in service, closure, owner change, or discovery of unregistered facility. | Minor | Review | 62-762
89 | Aboveground | 7003 | 62-762.401(4), 62-762.401(4)(a), 62-762.401(4)(a)1, 62-762.401(4)(a)2, 62-762.401(4)(b), 62-762.401(4)(c), 62-762.401(4)(d), 62-762.401(4)(e), 62-762.401(4)(f), 62-762.401(4)(g), 62-762.401(4)(h), 62-762.401(4)(i) | Registration fees not paid (not receiving fuel). | Minor | Review | 62-762
90 | Aboveground | 7004 | 62-762.401(5) | Placard not displayed (or available upon request). | Minor | Review | 62-762
91 | Aboveground | 7005 | 62-762.411(1)(b), 62-762.411(1)(c), 62-762.411(2), 62-762.411(2)(a), 62-762.411(2)(b), 62-762.411(2)(c) | Notification of installation, closure, or change in service status not received in required timeframes. | Minor | NCLI | 62-762
92 | Aboveground | 7006 | 62-762.411(3) | Notification of internal inspection not received in an timely manner. | Minor | NCLI | 62-762
93 | Aboveground | 7007 | 62-762.411(4) | Incident Notification Form (INF) not received in a timely manner. | Minor | NCLI | 62-762
94 | Aboveground | 7008 | 62-762.411(5) | Discharge Notification Form (DRF) not received in a timely manner. | SNC-B | NCLI | 62-762
95 | Aboveground | 7009 | 62-762.421(2), 62-762.421(3)(c) | No financial responsibility instrument or expired instrument for < 180 days. | SNC-B | Review | 62-762
96 | Aboveground | 7010 | 62-762.421(2), 62-762.421(3)(c) | No financial responsibility instrument or expired instrument for > 180 days. | SNC-A | Review | 62-762
97 | Aboveground | 7011 | 62-762.421(3), 62-762.421(3)(a), 62-762.421(3)(d), 62-762.421(3)(d)1, 62-762.421(3)(d)2, 62-762.421(3)(d)3, 62-762.421(3)(d)4, 62-762.421(8) | Appropriate paperwork for financial responsibility improperly completed or maintained. | Minor | Review | 62-762
98 | Aboveground | 7012 | 62-762.431(2) | Incident investigation not initiated within 24-hours (or by next business day) to determine if discharge occurred. | SNC-B | NCLI | 62-762
99 | Aboveground | 7013 | 62-762.431(4), 62-762.431(5) | Incident investigation leading to discharge not completed within 14 days, or No DRF or written confirmation received after 14 day investigation period. | Minor | Review | 62-762
100 | Aboveground | 7014 | 62-762.431(6) | Removal of regulated substance from a release not initiated within three days and completed within 30 days of discovery. | SNC-B | NCLI | 62-762
101 | Aboveground | 7015 | 62-762.431(8) | All incident records, including test results not kept until storage tank system closure. | Minor | NCLI | 62-762
102 | Aboveground | 7016 | 62-762.441(2) | Discharge not reported with 24-hours, or by next business day. | SNC-B | NCLI | 62-762
103 | Aboveground | 7017 | 62-762.441(3) | Analyticals not submitted with 24 -hours or next business day. OVA readings are not considered confirmation of discharge. | Minor | Review | 62-762
104 | Aboveground | 7018 | 62-762.441(6), 62-762.441(6)(a), 62-762.441(6)(b), 62-762.441(6)(c), 62-762.441(6)(d), 62-762.441(6)(e), 62-762.441(6)(f), 62-762.441(6)(g) | Actions not taken immediately to contain, remove, and abate the discharge. | SNC-A | Review | 62-762
105 | Aboveground | 7019 | 62-762.501(1)(b), 62-762.501(1)(b)1, 62-762.501(1)(b)1.a, 62-762.501(1)(b)1.b, 62-762.501(1)(b)1.c, 62-762.502(1)(b), 62-762.502(1)(b)1, 62-762.502(1)(b)1.a, 62-762.502(1)(b)1.b, 62-762.502(1)(b)1.c | Failure of secondary containment materials to meet standards. | SNC-B | Inspection | 62-762
106 | Aboveground | 7020 | 62-762.501(1)(b)8, 62-762.501(1)(b)9, 62-762.501(1)(b)10, 62-762.501(1)(b)11, 62-762.502(1)(b)8, 62-762.502(1)(b)9, 62-762.502(1)(b)10 | Integrity Testing of secondary containment systems and interstitial spaces not performed before being placed into service. | Minor | Inspection | 62-762
107 | Aboveground | 7021 | 62-762.501(1)(b)2, 62-762.502(1)(b)2 | Secondary containment using synthetic liners not in accordance with standards or not impervious. | Minor | Inspection | 62-762
108 | Aboveground | 7022 | 62-762.501(1)(b)3, 62-762.501(1)(b)3.a, 62-762.501(1)(b)3.b, 62-762.501(1)(b)3.c, 62-762.501(1)(b)4, 62-762.502(1)(b)3, 62-762.502(1)(b)3.a, 62-762.502(1)(b)3.b, 62-762.502(1)(b)3.c, 62-762.502(1)(b)4 | Secondary containment constructed of concrete not in accordance with standards or not impervious. | Minor | Inspection | 62-762
109 | Aboveground | 7023 | 62-762.501(1)(b)5, 62-762.502(1)(b)5 | VCI inhibitors are not contained by secondary containment system. | Minor | Review | 62-762
110 | Aboveground | 7024 | 62-762.501(1)(b)6, 62-762.502(1)(b)6 | Cathodically protected tanks and piping; secondary containment interferes with the operation of cathodic protection system. | Minor | Inspection | 62-762
111 | Aboveground | 7025 | 62-762.501(1)(b)7, 62-762.502(1)(b)7 | Secondary containment systems shall be designed and installed to direct any release to a monitoring point or points. | Minor | Inspection | 62-762
112 | Aboveground | 7026 | 62-762.501(1)(c), 62-762.501(1)(c)1, 62-762.501(1)(c)2, 62-762.502(1)(c), 62-762.502(1)(c)1 | Cathodic protection test station/method and operation does not meet standards. Or, secondary containment interferes with the cathodic protection system. | SNC-B | Inspection | 62-762
113 | Aboveground | 7027 | 62-762.501(1)(c)3, 62-762.502(1)(c)3 | Field installed cathodic protection not designed or installed by CP. | Minor | Inspection | 62-762
114 | Aboveground | 7028 | 62-762.501(1)(d), 62-762.501(1)(d)1, 62-762.501(1)(d)2, 62-762.502(1)(d), 62-762.502(1)(d)1, 62-762.502(1)(d)2 | Vapor Corrosion Inhibitors are not designed or installed by a Corrosion Professional and manufacturer for shop fabricated or field-erected tanks. | Minor | NCLI | 62-762
115 | Aboveground | 7029 | 62-762.501(1)(e), 62-762.502(1)(e) | The primary and secondary wall linings are not compatible with the regulated substance. | SNC-B | Review | 62-762
116 | Aboveground | 7030 | 62-762.501(1)(f), 62-762.502(1)(f) | Exterior coatings not protected from external corrosion, deterioration or degradation. | Minor | Inspection | 62-762
117 | Aboveground | 7031 | 62-762.501(1)(i), 62-762.502(1)(i) | Any component(s) of storage tank system not installed according to manufacturer's instructions. | Minor | Inspection | 62-762
118 | Aboveground | 7032 | 62-762.501(1)(g), 62-762.502(1)(g) | Any component(s) of storage tank system not installed according to reference standards. | SNC-B | Inspection | 62-762
119 | Aboveground | 7033 | 62-762.501(1)(h), 62-762.501(1)(h)1, 62-762.501(1)(h)2, 62-762.501(1)(h)3, 62-762.501(1)(h)4 | No signed or sealed survey drawing of the installed or relocated integral piping in contact with the soil. | Minor | Review | 62-762
120 | Aboveground | 7034 | 62-762.502(1)(h), 62-762.501(2), 62-762.501(2)(a) | Storage Tanks are not installed according to applicable provisions. | SNC-B | Inspection | 62-762
121 | Aboveground | 7035 | 62-762.501(2)(b), 62-762.501(2)(b)1, 62-762.501(2)(b)1.a, 62-762.501(2)(b)1.b, 62-762.501(2)(b)1.c, 62-762.501(2)(b)1.d, 62-762.501(2)(b)1.e, 62-762.501(2)(b)1.f, 62-762.501(2)(b)1.g, 62-762.501(2)(b)1.h, 62-762.501(2)(b)2, 62-762.502(2), 62-762.502(2)(a), 62-762.502(2)(b), 62-762.502(2)(b)1, 62-762.502(2)(b)1.a, 62-762.502(2)(b)1.b, 62-762.502(2)(b)2 | Storage tanks not constructed according to manufacturer's instructions or reference standards or meet inspection schedule established. | SNC-B | Inspection | 62-762
122 | Aboveground | 7036 | 62-762.501(2)(c), 62-762.501(2)(c)1, 62-762.502(2)(c), 62-762.502(2)(c)1, 62-762.502(2)(c)2 | Cathodic protection installation does not meet requirements. | SNC-B | Inspection | 62-762
123 | Aboveground | 7037 | 62-762.501(2)(c)3, 62-762.502(2)(c)3 | Cathodic protection system not installed with test station or monitoring point. | Minor | Inspection | 62-762
124 | Aboveground | 7038 | 62-762.501(2)(c)5, 62-762.502(2)(c)5 | VCI not installed according to requirements. | Minor | Inspection | 62-762
125 | Aboveground | 7039 | 62-762.501(2)(d), 62-762.501(2)(d)1, 62-762.501(2)(d)2, 62-762.501(2)(d)3, 62-762.501(2)(d)3.a, 62-762.501(2)(d)3.b, 62-762.501(2)(d)3.c, 62-762.501(2)(d)3.c.(I), 62-762.501(2)(d)3.c.(II), 62-762.501(2)(d)3.d, 62-762.502(2)(d), 62-762.502(2)(d)1, 62-762.502(2)(d)2, 62-762.502(2)(d)3, 62-762.502(2)(d)3.a, 62-762.502(2)(d)3.b, 62-762.502(2)(d)3.c, 62-762.502(2)(d)3.d, 62-762.502(2)(d)4, 62-762.502(2)(d)5, 62-762.502(2)(d)6, 62-762.502(2)(d)7 | Secondary containment not installed per standards, including capacity requirements, drainage, and seal. | SNC-B | Inspection | 62-762
126 | Aboveground | 7040 | 62-762.501(2)(e), 62-762.501(2)(e)1, 62-762.501(2)(e)2, 62-762.501(2)(e)2.a, 62-762.501(2)(e)2.b, 62-762.501(2)(e)2.c, 62-762.501(2)(e)2.d, 62-762.502(2)(e), 62-762.502(2)(e)1, 62-762.502(2)(e)2, 62-762.502(2)(e)3, 62-762.502(2)(e)3.a, 62-762.502(2)(e)3.b, 62-762.502(2)(e)3.c, 62-762.502(2)(e)3.d, 62-762.501(2)(e)5 | Overfill protection not provided. Fuel transfer not monitored. Alarms not installed. | SNC-B | Inspection | 62-762
127 | Aboveground | 7041 | 62-762.501(2)(e)3, 62-762.501(2)(e)3.a, 62-762.501(2)(e)3.b, 62-762.501(2)(e)4, 62-762.502(2)(e)4, 62-762.502(2)(e)4.a, 62-762.502(2)(e)4.b, 62-762.502(2)(e)5 | Failure to designate, register, or annually test primary overfill protection device, | Minor | Review | 62-762
128 | Aboveground | 7042 | 62-762.501(2)(f), 62-762.501(2)(f)1, 62-762.502(2)(f) | Storage tank system not installed with a spill containment system at each tank fill connection. Does not meet performance requirements. | SNC-B | Inspection | 62-762
129 | Aboveground | 7043 | 62-762.501(2)(f)2 | Fillbox covers not marked according to requirements. | Minor | Inspection | 62-762
130 | Aboveground | 7044 | 62-762.501(2)(f)3 | Spill containment systems not installed to allow for release detection. | SNC-B | Inspection | 62-762
131 | Aboveground | 7045 | 62-762.501(2)(g), 62-762.501(2)(g)1 | Dispensers not installed and maintained according to standards. | Minor | Inspection | 62-762
132 | Aboveground | 7046 | 62-762.501(2)(g)2, 62-762.501(2)(g)3 | Dispensers not installed with a dispenser sump, or allow for release detection. | SNC-B | Inspection | 62-762
133 | Aboveground | 7047 | 62-762.501(2)(h), 62-762.501(2)(h)1, 62-762.502(2)(g), 62-762.502(2)(g)1 | Piping sumps not meeting performance requirements or installed to allow for release detection. | SNC-B | Inspection | 62-762
134 | Aboveground | 7048 | 62-762.501(2)(h)2, 62-762.502(2)(g)2 | Piping sumps not installed to allow for release detection. | SNC-B | Inspection | 62-762
135 | Aboveground | 7049 | 62-762.501(2)(i), 62-762.502(2)(h) | Hydrant sumps not installed or registered. | SNC-B | Inspection | 62-762
136 | Aboveground | 7050 | 62-762.501(2)(j), 62-762.502(2)(i) | Aboveground storage tank system relocation requirements not met, not properly recertified, or does not meet current standards. | SNC-B | Inspection | 62-762
137 | Aboveground | 7051 | 62-762.501(3), 62-762.501(3)(a), 62-762.501(3)(a)1 | Pressurized piping or secondarily contained piping in contact with soil does not have appropriate testing, including breach of integrity, tightness or electronic leak detection. | SNC-B | Inspection | 62-762
138 | Aboveground | 7052 | 62-762.501(3)(a)2 | No interstitial integrity test on piping in contact with the soil before being placed in service. | SNC-B | Review | 62-762
139 | Aboveground | 7053 | 62-762.501(3)(a)3 | New integral piping not in contact with soil does not meet construction requirements. | SNC-B | Inspection | 62-762
140 | Aboveground | 7054 | 62-762.501(3)(a)4 | Integral piping not installed with a slope. | Minor | Inspection | 62-762
141 | Aboveground | 7055 | 62-762.501(3)(a)5, 62-762.501(3)(a)6 | Pressurized piping not installed with line leak detectors or does not meet requirements of paragraph 62-762.601(4)(b). | SNC-B | Inspection | 62-762
142 | Aboveground | 7056 | 62-762.501(3)(b), 62-762.501(3)(b)1, 62-762.501(3)(b)2, 62-762.501(3)(b)3 | Secondary containment not provided for small diameter integral piping. | SNC-B | Inspection | 62-762
143 | Aboveground | 7057 | 62-762.501(3)(c), 62-762.501(3)(c)1, 62-762.501(3)(c)2, 62-762.501(3)(c)3, 62-762.501(3)(c)4, 62-762.501(3)(c)5 | Piping in contact with soil not installed to standards. | SNC-B | Inspection | 62-762
144 | Aboveground | 7058 | 62-762.501(3)(d)1, 62-762.501(3)(d)2, 62-762.501(3)(d)3 | Valves do not meet standards of Section 7 of PEI/RP200-13 for piping systems with gravity head. | Minor | Inspection | 62-762
145 | Aboveground | 7059 | 62-762.502(4), 62-762.502(4)(a), 62-762.502(4)(a)1, 62-762.502(4)(a)2 | Bulk product piping not installed per manufacturer's instructions, or reference standards. Testing not completed prior to service. | SNC-B | Inspection | 62-762
146 | Aboveground | 7060 | 62-762.502(4)(a)3 | Integrity test not performed for underground bulk product piping for high viscosity products. | SNC-B | Review | 62-762
147 | Aboveground | 7061 | 62-762.502(4)(b), 62-762.502(4)(b)1, 62-762.502(4)(b)2, 62-762.502(4)(b)3, 62-762.502(4)(b)4, 62-762.502(4)(b)5 | Bulk product piping: Failure of secondary containment to meet standards for field erected tank systems. | SNC-B | Review | 62-762
148 | Aboveground | 7062 | 62-762.502(4)(c), 62-762.502(4)(c)1, 62-762.502(4)(c)2, 62-762.502(4)(c)3 | Bulk product piping not constructed according to reference standards or meet inspection schedule established. | SNC-B | Inspection | 62-762
149 | Aboveground | 7063 | 62-762.601(1), 62-762.601(1)(a), 62-762.601(1)(b), 62-762.601(1)(c), 62-762.602(1), 62-762.602(1)(a), 62-762.602(1)(b), 62-762.602(1)(c) | Storage tank systems does not have appropriate testing, including breach of integrity, tightness or electronic leak detection. | SNC-A | Inspection | 62-762
150 | Aboveground | 7064 | 62-762.601(1)(d), 62-762.601(1)(g), 62-762.602(1)(d), 62-762.602(1)(g) | Release detection not tested or visually inspected once a month or problems found during the visual inspections not recorded. | Minor | Review | 62-762
151 | Aboveground | 7065 | 62-762.601(1)(e), 62-762.602(1)(e) | Storage tank system not visually inspected once a month. | SNC-B | Review | 62-762
152 | Aboveground | 7066 | 62-762.601(1)(f), 62-762.602(1)(f), 62-762.601(1)(f)1, 62-762.602(1)(f)1 | Electronic and mechanical release detection not installed, calibrated, operated and maintained per manufacturer's specifications. | SNC-B | Review | 62-762
153 | Aboveground | 7067 | 62-762.601(1)(f)2, 62-762.602(1)(f)2 | Electronic and mechanical release detection not registered. | Minor | Review | 62-762
154 | Aboveground | 7068 | 62-762.601(1)(h), 62-762.602(1)(h) | Release detection not properly installed. | SNC-B | Review | 62-762
155 | Aboveground | 7069 | 62-762.601(2), 62-762.601(2)(a), 62-762.601(2)(a)1, 62-762.601(2)(a)2, 62-762.601(2)(a)3, 62-762.601(2)(a)4, 62-762.601(2)(a)5, 62-762.601(2)(a)6, 62-762.601(2)(a)7, 62-762.601(2)(a)8, 62-762.602(2), 62-762.602(2)(a), 62-762.602(2)(a)1, 62-762.602(2)(a)2, 62-762.602(2)(a)3, 62-762.602(2)(a)4, 62-762.602(2)(a)5, 62-762.602(2)(a)6, 62-762.602(2)(a)7, 62-762.602(2)(a)8 | Release detection does not meet standards. | SNC-B | Inspection | 62-762
156 | Aboveground | 7070 | 62-762.601(3), 62-762.601(3)(a), 62-762.601(3)(b), 62-762.602(3), 62-762.602(3)(a), 62-762.602(3)(a)1, 62-762.602(3)(a)2, 62-762.602(3)(a)2.a, 62-762.602(3)(a)2.b, 62-762.602(3)(a)2.c | Storage tanks without secondary containment not visually inspected monthly. | SNC-B | Inspection | 62-762
157 | Aboveground | 7071 | 62-762.601(4), 62-762.601(4)(a), 62-762.601(4)(b), 62-762.601(4)(b)1, 62-762.601(4)(b)2, 62-762.601(4)(b)3 | Small diameter integral piping with secondary containment: Applicable release detection methods not used. | SNC-B | Review | 62-762
158 | Aboveground | 7072 | 62-762.601(7), 62-762.602(7) | Annual operability testing of release detection systems not completed. | Minor | Review | 62-762
159 | Aboveground | 7073 | 62-762.602(3)(b), 62-762.602(3)(b)1, 62-762.602(3)(b)2 | No monthly visual inspection of aboveground or exempt bulk product pipe. Electronic sensing equipment not tested annually. | SNC-B | Review | 62-762
160 | Aboveground | 7074 | 62-762.602(6), 62-762.602(6)(a), 62-762.602(6)(b), 62-762.602(6)(c), 62-762.602(6)(d) | Bulk product and hydrant piping without secondary containment does not have annual testing or visual inspections completed monthly. | SNC-B | Review | 62-762
161 | Aboveground | 7075 | 62-762.701(1), 62-762.701(1)(a), 62-762.701(1)(a)1, 62-762.701(1)(a)2, 62-762.701(1)(a)3, 62-762.702(1), 62-762.702(1)(a), 62-762.702(1)(a)1, 62-762.702(1)(a)2, 62-762.702(1)(a)3 | Not repaired component or piping which has not caused a discharge or release. | SNC-B | Inspection | 62-762
162 | Aboveground | 7076 | 62-762.701(1), 62-762.701(1)(a), 62-762.701(1)(a)1, 62-762.701(1)(a)2, 62-762.701(1)(a)3, 62-762.702(1), 62-762.702(1)(a), 62-762.702(1)(a)1, 62-762.702(1)(a)2, 62-762.702(1)(a)3 | Not repaired component or piping which has cause a discharge or release. | SNC-A | Inspection | 62-762
163 | Aboveground | 7077 | 62-762.701(1)(b), 62-762.701(1)(b)1, 62-762.701(1)(b)2, 62-762.701(1)(b)3, 62-762.702(1)(b), 62-762.702(1)(b)1, 62-762.702(1)(b)2, 62-762.702(1)(b)3 | Damaged system not taken out of service until repairs are made. | SNC-B | Inspection | 62-762
164 | Aboveground | 7078 | 62-762.701(1)(c), 62-762.701(1)(c)1, 62-762.701(1)(c)2, 62-762.702(1)(c), 62-762.702(1)(c)1, 62-762.702(1)(c)2 | System not repaired in accordance with manufacturer's instructions or applicable requirements. | Minor | Inspection | 62-762
165 | Aboveground | 7079 | 62-762.701(1)(d) | Repairs not completed per applicable standards. | Minor | Inspection | 62-762
166 | Aboveground | 7080 | 62-762.701(1)(e), 62-762.702(1)(d) | Repaired components not integrity tested before being placed back into operation. | Minor | Inspection | 62-762
167 | Aboveground | 7081 | 62-762.701(1)(f), 62-762.701(1)(f)1, 62-762.701(1)(f)2, 62-762.702(1)(e), 62-762.702(1)(e)1, 62-762.702(1)(e)2 | Piping that is damaged which has not caused a discharge is not replaced. | SNC-B | Inspection | 62-762
168 | Aboveground | 7082 | 62-762.701(1)(f), 62-762.701(1)(f)1, 62-762.701(1)(f)2, 62-762.702(1)(e), 62-762.702(1)(e)1, 62-762.702(1)(e)2 | Piping that is damaged which has caused a discharge is not replaced. | SNC-A | Inspection | 62-762
169 | Aboveground | 7083 | 62-762.701(1)(g), 62-762.702(1)(f) | Storage tank system not taken out-of-service when repairs cannot be made within 90 days. | SNC-B | Inspection | 62-762
170 | Aboveground | 7084 | 62-762.701(2), 62-762.701(2)(a), 62-762.702(2), 62-762.702(2)(a) | Cathodic and corrosion protection not operated and maintained to provide continuous protection, including inspection schedule. Not take out of service when requirement not met. | Minor | Inspection | 62-762
171 | Aboveground | 7085 | 62-762.701(2)(b), 62-762.701(2)(b)1, 62-762.701(2)(b)2, 62-762.702(2)(b), 62-762.702(2)(b)1, 62-762.702(2)(b)2 | Cathodic protection not inspected, tested and evaluated within six months of installation or repair, and at least yearly. Factory installed cathodic protection not tested, inspected or evaluated every 3 years. | Minor | Review | 62-762
172 | Aboveground | 7086 | 62-762.701(2)(c), 62-762.702(2)(c) | Inpressed current and cathodic protection records not maintained. | Minor | Review | 62-762
173 | Aboveground | 7087 | 62-762.701(2)(d), 62-762.701(2)(d)1, 62-762.701(2)(d)2, 62-762.702(2)(d), 62-762.702(2)(d)1, 62-762.702(2)(d)2 | Cathodic protection systems cannot achieve or maintain protection, not repaired or closed in timeframes. | Minor | Inspection | 62-762
174 | Aboveground | 7088 | 62-762.701(3), 62-762.701(3)(a), 62-762.701(3)(b), 62-762.701(3)(b)1, 62-762.701(3)(b)2, 62-762.701(3)(c), 62-762.701(3)(d), 62-762.701(3)(d)1, 62-762.701(3)(d)2, 62-762.702(3), 62-762.702(3)(a), 62-762.702(3)(b), 62-762.702(3)(b)1, 62-762.702(3)(b)2, 62-762.702(3)(c), 62-762.702(3)(d), 62-762.702(3)(d)1, 62-762.702(3)(d)2 | Vapor corrosion inhibitor not operated and maintained to provide continuous protection, including inspection schedule. Not take out of service when requirement not met. | Minor | Review | 62-762
175 | Aboveground | 7089 | 62-762.701(4), 62-762.701(4)(a), 62-762.701(4)(a)1, 62-762.701(4)(a)1.a, 62-762.701(4)(a)1.b, 62-762.701(4)(a)1.c, 62-762.701(4)(a)1.d, 62-762.701(4)(a)1.e, 62-762.701(4)(a)1.f, 62-762.701(4)(a)2, 62-762.702(4), 62-762.702(4)(a), 62-762.702(4)(a)1, 62-762.702(4)(a)1.a, 62-762.702(4)(a)1.b, 62-762.702(4)(a)1.c, 62-762.702(4)(a)1.d, 62-762.702(4)(a)2 | Integrity testing of secondary containment systems and interstitial spaces not performed per schedule. | Minor | Review | 62-762
176 | Aboveground | 7090 | 62-762.701(4)(b), 62-762.701(4)(b)1, 62-762.701(4)(b)2, 62-762.702(4)(b), 62-762.702(4)(b)1, 62-762.702(4)(b)2 | Spill containment, dispenser liners and piping sumps not accessible; water and regulated substances not removed. | Minor | Review | 62-762
177 | Aboveground | 7091 | 62-762.701(4)(c), 62-762.702(4)(c) | Exterior Coatings not maintained to prevent corrosion. | Minor | Inspection | 62-762
178 | Aboveground | 7092 | 62-762.701(5), 62-762.701(5)(a), 62-762.701(5)(b), 62-762.701(5)(b)1, 62-762.701(5)(b)2, 62-762.701(5)(c), 62-762.701(5)(d), 62-762.702(5), 62-762.702(5)(a), 62-762.702(5)(b), 62-762.702(5)(b)1, 62-762.702(5)(b)2, 62-762.702(5)(c), 62-762.702(5)(d) | Stormwater not drawn off within one week. | Minor | Review | 62-762
179 | Aboveground | 7093 | 62-762.702(6), 62-762.702(7) | Evaluation and testing not conducted in accordance with API standards or by a Florida licensed engineer. | Minor | Review | 62-762
180 | Aboveground | 7094 | 62-762.711(1) | Permanent records not available within 5 working days notice. | Minor | Review | 62-762
181 | Aboveground | 7095 | 62-762.711(2), 62-762.711(2)(a), 62-762.711(2)(b), 62-762.711(2)(c), 62-762.711(2)(d) | Records requiring 3 year documentation period not kept by facility. | Minor | Review | 62-762
182 | Aboveground | 7096 | 62-762.711(3), 62-762.711(3)(a), 62-762.711(3)(b), 62-762.711(3)(c), 62-762.711(3)(d), 62-762.711(3)(e), 62-762.711(3)(f), 62-762.711(3)(g), 62-762.711(3)(h), 62-762.711(3)(i), 62-762.711(3)(j) | Records not kept until closure of system. | Minor | Review | 62-762
183 | Aboveground | 7097 | 62-762.801(1), 62-762.801(1)(a), 62-762.801(1)(b), 62-762.801(1)(b)1, 62-762.801(1)(b)2, 62-762.801(1)(b)3, 62-762.801(1)(b)4, 62-762.801(1)(b)5, 62-762.801(1)(b)6, 62-762.802(2), 62-762.802(2)(a), 62-762.802(2)(b), 62-762.802(2)(b)1, 62-762.802(2)(b)2, 62-762.802(2)(b)3, 62-762.802(2)(b)4, 62-762.802(2)(b)5, 62-762.802(2)(b)6 | Requirements not met for out of service systems including registering system out-of-service and securing out-of-service system. | Minor | Inspection | 62-762
184 | Aboveground | 7098 | 62-762.801(1)(c)4, 62-762.801(1)(c)4.a, 62-762.801(1)(c)4.b, 62-762.802(2)(d)3, 62-762.802(2)(d)3.a, 62-762.802(2)(d)3.b | Testing shall be up-to-date and indicate proper operation before adding regulated substances to the storage tank system or returning system to service. | Minor | Review | 62-762
185 | Aboveground | 7099 | 62-762.801(1)(d), 62-762.802(2)(e) | System with secondary containment out of service greater than 10 years. | SNC-B | Review | 62-762
186 | Aboveground | 7100 | 62-762.801(1)(e), 62-762.802(2)(f) | System without secondary containment out of service greater than 5 years. | SNC-B | Review | 62-762
187 | Aboveground | 7101 | 62-762.801(2), 62-762.801(2)(a), 62-762.801(2)(a)1, 62-762.801(2)(a)1.a, 62-762.801(2)(a)1.b, 62-762.801(2)(a)2, 62-762.801(2)(a)3, 62-762.801(2)(a)4, 62-762.802(3), 62-762.802(3)(a), 62-762.802(3)(a)1, 62-762.802(3)(a)1.a, 62-762.802(3)(a)1.b, 62-762.802(3)(a)2, 62-762.802(3)(a)3, 62-762.802(3)(a)4 | Storage tank system not closed within 90 days in accordance with this subsection. | SNC-B | Review | 62-762
188 | Aboveground | 7102 | 62-762.801(2)(b), 62-762.801(2)(b)1, 62-762.801(2)(b)2, 62-762.801(2)(b)3, 62-762.801(2)(b)4, 62-762.801(2)(b)5, 62-762.801(2)(b)6, 62-762.801(2)(b)7, 62-762.802(3)(b), 62-762.802(3)(b)1, 62-762.802(3)(b)2, 62-762.802(3)(b)3, 62-762.802(3)(b)4, 62-762.802(3)(b)5, 62-762.802(3)(b)6, 62-762.802(3)(b)7 | Closure Integrity Report and Evaluation not completed and submitted in a timely fashion. | Minor | Inspection | 62-762
189 | Aboveground | 7103 | 62-762.801(2)(b)8, 62-762.802(3)(b)8 | Registration not updated for closure of storage tank system. | Minor | Review | 62-762
190 | Aboveground | 7104 | 62-762.801(3), 62-762.801(3)(a), 62-762.801(3)(a)1, 62-762.801(3)(a)2, 62-762.801(3)(a)3, 62-762.801(3)(a)4, 62-762.801(3)(a)5, 62-762.801(3)(a)6, 62-762.801(3)(a)7, 62-762.802(4), 62-762.802(4)(a), 62-762.802(4)(a)1, 62-762.802(4)(a)2, 62-762.802(4)(a)3, 62-762.802(4)(a)4, 62-762.802(4)(a)5, 62-762.802(4)(a)6, 62-762.802(4)(a)7 | Closure integrity Report not submitted. | Minor | Review | 62-762
191 | Aboveground | 7105 | 62-762.801(3)(b), 62-762.802(4)(b) | Closure Report not submitted. | Minor | Review | 62-762
192 | Aboveground | 7106 | 62-762.801(3)(c), 62-762.801(3)(c)1, 62-762.801(3)(c)2, 62-762.801(3)(c)3, 62-762.802(4)(c), 62-762.802(4)(c)1, 62-762.802(4)(c)2, 62-762.802(4)(c)3 | Limited Closure Report not submitted. | Minor | Review | 62-762
193 | Aboveground | 7107 | 62-762.802(1), 62-762.802(1)(a), 62-762.802(1)(b), 62-762.802(1)(c), 62-762.802(1)(d) | Requirements not met for field-erected tanks placed temporarily out of service. | Minor | Review | 62-762
194 | Aboveground | 7108 | 62-762.802(2)(c) | Out of service bulk or field-erected storage tank systems not monitored annually. | Minor | Review | 62-762
195 | Aboveground | 7109 | 62-762.802(2)(g), 62-762.851(1), 62-762.851(1)(a), 62-762.851(1)(b), 62-762.851(1)(b)1, 62-762.851(1)(b)2, 62-762.851(1)(b)3, 62-762.851(1)(b)4, 62-762.851(1)(b)5, 62-762.851(1)(b)6, 62-762.851(1)(b)7, 62-762.851(1)(c), 62-762.851(1)(c)1, 62-762.851(1)(c)2, 62-762.851(1)(d), 62-762.851(1)(e), 62-762.851(1)(f) | Facility not in compliance with Alternate Procedures. | Minor | Review | 62-762
196 | Aboveground | 7110 | 62-762.851(2), 62-762.851(2)(a), 62-762.851(2)(b), 62-762.851(2)(c), 62-762.851(2)(d), 62-762.851(2)(e), 62-762.851(2)(f), 62-762.851(2)(f)1, 62-762.851(2)(f)2, 62-762.851(2)(f)3, 62-762.851(2)(f)4, 62-762.851(2)(f)5, 62-762.851(2)(f)6, 62-762.851(2)(g), 62-762.851(2)(h), 62-762.851(2)(i), 62-762.851(2)(i)1, 62-762.851(2)(i)2, 62-762.851(2)(i)3 | Equipment not registered with DEP before installation or use. | Minor | Review | 62-762
197 | Aboveground | 7111 | 62-762.891(3), 62-762.891(3)(a), 62-762.891(3)(b) | Mineral acid tank systems not registered. | Minor | Review | 62-762
198 | Aboveground | 7112 | 62-762.891(3)(c) | No notification of change of registration information for Mineral Acid Tank. | Minor | Review | 62-762
199 | Aboveground | 7113 | 62-762.891(3)(d), 62-762.891(3)(d)1, 62-762.891(3)(d)2, 62-762.891(4), 62-762.891(4)(a), 62-762.891(4)(b), 62-762.891(4)(b)1, 62-762.891(4)(b)1.a, 62-762.891(4)(b)1.b, 62-762.891(4)(b)1.c, 62-762.891(4)(b)2 | Improper registration for Mineral Acid Tank. | Minor | Review | 62-762
200 | Aboveground | 7114 | 62-762.891(4)(c) | Placard not displayed for Mineral Acid Tank. | Minor | Review | 62-762
201 | Aboveground | 7115 | 62-762.891(5), 62-762.891(5)(a) | County not notified of CIP or secondary containment, by PE for Mineral Acid Tank. | Minor | Review | 62-762
202 | Aboveground | 7116 | 62-762.891(5)(b) | Incident notification not submitted within 72-hours. | Minor | Review | 62-762
203 | Aboveground | 7117 | 62-762.891(5)(c), 62-762.891(5)(c)1, 62-762.891(5)(c)2, 62-762.891(5)(c)3 | Mineral Acid Tank: Discharge not reported with 24-hours, or by next business day. | SNC-B | Review | 62-762
204 | Aboveground | 7118 | 62-762.891(6), 62-762.891(6)(a), 62-762.891(6)(a)1, 62-762.891(6)(a)2 | No secondary containment or CIP for mineral acid tanks. | SNC-B | Review | 62-762
205 | Aboveground | 7119 | 62-762.891(6)(b), 62-762.891(6)(b)1, 62-762.891(6)(b)2, 62-762.891(6)(b)3 | Secondary containment for Mineral Acid Tank not certified by PE. | Minor | Review | 62-762
206 | Aboveground | 7120 | 62-762.891(6)(c), 62-762.891(6)(c)1 | CIP not certified by PE. | Minor | Review | 62-762
207 | Aboveground | 7121 | 62-762.891(6)(c)2, 62-762.891(6)(c)2.a, 62-762.891(6)(c)2.b, 62-762.891(6)(c)2.c, 62-762.891(6)(c)2.d, 62-762.891(6)(c)2.e, 62-762.891(6)(c)2.f, 62-762.891(6)(c)2.g, 62-762.891(6)(c)2.h, 62-762.891(6)(c)2.i | CIP for Mineral Acid Tank does not meet requirements or certified by PE. | Minor | Review | 62-762
208 | Aboveground | 7122 | 62-762.891(7), 62-762.891(7)(a), 62-762.891(7)(b), 62-762.891(7)(c) | Records not kept for Mineral Acid Tank(s). | Minor | Review | 62-762
209 | Aboveground | 7123 | 62-762.891(8), 62-762.891(8)(a), 62-762.891(8)(a)1, 62-762.891(8)(a)2, 62-762.891(8)(a)3, 62-762.891(8)(b) | Appropriate actions not taken in the event of a discharge. | SNC-A | Inspection | 62-762
209 | Aboveground | 7125 | 62-762.401(5) | Owner, operator, or supplier deposited motor fuel into storage tank without current valid registration placard. | SNC-A | Review | 62-762